## Executive_Summary
APAC HYPERSCALE DATA CENTER LIGHTNING RISK ASSESSMENT & PROTECTION WORKBOOK (v2.5.0)
Pre-Calibrated for Hong Kong (EMSD), Indonesia (SNI 03-7015 / Reference), and Malaysia (MS IEC 62305) ¦ 100% Formula-Driven per IEC 62305-2:2010 & BS EN 62305-2:2012
HONG KONG DC (TKO) |  | INDONESIA REF (BASELINE) |  | INDONESIA CIKARANG (TD=140) |  | MALAYSIA JOHOR DC (TD=165) |  | STATUTORY LIMIT (RT1)
1
R1 (×10⁻⁵) ¦ Class I LPS PASS |  | R1 (×10⁻⁵) ¦ Reproduces 0.72e-5 |  | R1 (×10⁻⁵) ¦ Class I Enhanced PASS |  | R1 (×10⁻⁵) ¦ Class I Enhanced PASS |  | Max Tolerable Life Risk (×10⁻⁵/yr)
1. Tri-Regional Data Center Risk Assessment Summary (Unprotected vs. Target Protected State)
Regional Facility Profile | Governing Code | Td (days/yr) | Ng (fl/km²/yr) | Collection Area AD (m²) | Direct Flashes ND (/yr) | Unprotected R1 (×10⁻⁵) | Protected R1 (×10⁻⁵) | Protected R2 (×10⁻³) | Compliance Status
Hong Kong SAR — TKO Hyperscale DC | EMSD CoP / BS EN 62305-2
Indonesia — Reference Reference Baseline | BS EN 62305-2:2012
Indonesia — Cikarang Tropical DC (High Strike) | SNI 03-7015 / IEC 62305-2
Malaysia — Johor Bahru / KL Hyperscale DC | MS IEC 62305 (ST)
2. Side-by-Side R1 Human Life Risk (×10⁻⁵/yr) Across All 5 LPS Protection Levels (Tolerable Limit RT1 = 1.00 × 10⁻⁵)
Regional Facility Profile | No Protection | Class IV LPS | Class III LPS | Class II LPS | Class I / Enhanced | Tolerable Limit RT1 | Rolling Sphere r (m) | Min Separation s (m) | Selected LPS Class
Hong Kong SAR — TKO Hyperscale DC | [5 empty] | 1
Indonesia — Reference Reference Baseline | [5 empty] | 1
Indonesia — Cikarang Tropical DC (High Strike) | [5 empty] | 1
Malaysia — Johor Bahru / KL Hyperscale DC | [5 empty] | 1
3. IEC 62305-2 Ed.2 Dual-Line (Power + Telecom + Adj NDJ) vs. Ed.3 Simplified Single-Line Mode Comparison
Regional Facility Profile | Ed.2 Unprotected R1 (×10⁻⁵) | Ed.3 Single-Line Unprotected R1 (×10⁻⁵) | Ed.2 Class I Protected R1 (×10⁻⁵) | Ed.3 Single-Line Protected R1 (×10⁻⁵) | Ed.3 vs Ed.2 Protected Delta (%) | Active Rolling Sphere r (m) | Rooftop Mast Protected Span rp (m) | Required Separation s = (ki/km)·kc·l (m) | Dual-Mode Compliance Status
Hong Kong SAR — TKO Hyperscale DC
Indonesia — Reference Reference Baseline
Indonesia — Cikarang Tropical DC (High Strike)
Malaysia — Johor Bahru / KL Hyperscale DC

## HKG_DataCenter
IEC 62305-2 / BS EN 62305-2 LIGHTNING RISK CALCULATION SHEET — HONG KONG SAR — TKO HYPERSCALE DATA CENTER (80m × 50m × 24m)
Governing Standard: EMSD CoP / BS EN 62305-2:2012 ¦ Meteorological Authority: Hong Kong Observatory (HKO) ¦ Dual-Line (Power + Telecom) & Adjacent Structure Model
Parameter / Risk Component Description | Symbol | IEC Clause / Ref | Unit / Mode | No Protection | Class IV LPS | Class III LPS | Class II LPS | Class I LPS (Target)
Structure Length | L | Annex A.2 | m | 80 | 80 | 80 | 80 | 80
Structure Width | W | Annex A.2 | m | 50 | 50 | 50 | 50 | 50
Structure Max Height | H | Annex A.2 | m | 24 | 24 | 24 | 24 | 24
Collection Area of Isolated Structure | AD | Eq. A.2 | m²
Location Factor of Structure | CD | Table A.1 | factor | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Thunderstorm Days per Year | TD | Meteorological | days/yr | 42 | 42 | 42 | 42 | 42
Lightning Ground Flash Density | NG | Eq. A.1 / Network | fl/km²/yr | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Annual Direct Flashes to Structure | ND | Eq. A.4 | events/yr
Collection Area of Flashes Near Structure | AM | Eq. A.7 | m²
Annual Flashes Near Structure | NM | Eq. A.6 | events/yr
Incoming Service Route Length (Power & Telecom) | LL | Table A.2 / E.2 | m | 500 | 500 | 500 | 500 | 500
Line Installation & Environmental Product (CI × CE × CT) | CI·CE·CT | Table A.2–A.4 | factor | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Adjacent Structure Collection Area & Events (NDJ) | NDJ | Eq. A.5 | events/yr
Annual Flashes to & Near Connected Line (NL / NI per service) | NL_P / NI_P | Eq. A.8 / A.10 | events/yr
Touch & Step Voltage Protection Factor | PTA | Table B.1 | prob | 1 | 0.01 | 0.01 | 0.01 | 0.01
Physical Damage Probability (External LPS Class) | PB | Table B.2 | prob | 1 | 0.2 | 0.1 | 0.05 | 0.02
Shock Probability from Direct Flash (PA = PTA × PB) | PA | Eq. B.1 | prob
Coordinated SPD Protection Probability (PC = PSPD × CLD) | PSPD / PC | Table B.3 | prob | 1 | 0.05 | 0.05 | 0.02 | 0.01
LPS Mesh Width & Spatial Shielding Factor (wm) | wm | IEC 62305-3 | m | 0 | 60 | 45 | 30 | 20
Internal Magnetic Surge Probability (PM = PSPD × PMS) | PM | Eq. B.4 | prob
Equipotential Bonding Probability at Line Entrance (PEB) | PEB / PV | Table B.7 | prob | 0.05 | 0.05 | 0.05 | 0.02 | 0.01
Service Line Shock Probability (PU = PTU × PEB × PLD × CLD) | PU | Eq. B.8 | prob
Induced Line Surge Failure Probability (PZ_P + PZ_T) | PZ_sum | Eq. B.11 | prob
Loss Factor for Touch & Step Shock (LA1 = rt × LT1 × nZ/nt) | LA1 | Eq. C.1 | loss | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001
Loss Factor for Physical Fire Damage (LB1 = LV1 = rp×rf×hz×LF1×nZ/nt) | LB1 / LV1 | Eq. C.3 | loss | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05
Loss Factor for Internal Systems Failure (LC1 / LC2 / LC4) | LC2 (Pub) | Eq. C.8 | loss | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
RA: Injury due to Touch & Step Voltage (Direct Strike S1) | RA (×10⁻⁵) | ND×PA×LA1 | ×10⁻⁵/yr
RB: Physical Fire Damage to Structure (Direct Strike S1) | RB (×10⁻⁵) | ND×PB×LB1 | ×10⁻⁵/yr
RC + RM: Failure of Internal Systems (S1 + S2) | RC+RM (×10⁻⁵) | IEC Table 2 | ×10⁻⁵/yr
RU (Power + Telecom): Injury via Incoming Service Lines (S3) | RU (×10⁻⁵) | 2×(NL+NDJ)×PU×LU1 | ×10⁻⁵/yr
RV (Power + Telecom): Physical Fire via Service Lines (S3) | RV (×10⁻⁵) | 2×(NL+NDJ)×PV×LV1 | ×10⁻⁵/yr
RW + RZ (Power + Telecom): Internal Failure via Lines (S3 + S4) | RW+RZ (×10⁻⁵) | IEC Table 2 | ×10⁻⁵/yr
TOTAL RISK R1: Loss of Human Life (Limit RT1 = 1.00 × 10⁻⁵) | R1 (×10⁻⁵) | Sum(RA..RZ) | ×10⁻⁵/yr
TOTAL RISK R2: Loss of Public Service (Limit RT2 = 1.00 × 10⁻³) | R2 (×10⁻³) | IEC Eq. 2 | ×10⁻³/yr
TOTAL RISK R4: Economic Value Loss (Limit RT4 = 1.00 × 10⁻³) | R4 (×10⁻³) | IEC Eq. 4 | ×10⁻³/yr
Statutory Compliance Verdict (R1 ≤ 1.00e-5 AND R2 ≤ 1.00e-3) | Verdict | IEC 62305-2 Sec 5.3 | PASS / FAIL
IEC 62305-2 Ed.3 Simplified Single-Line Mode R1 (1 Line, No Adj NDJ) | R1_Ed3 (×10⁻⁵) | Ed.3 Single-Line | ×10⁻⁵/yr

## IDN_Ref_Baseline
IEC 62305-2 / BS EN 62305-2 LIGHTNING RISK CALCULATION SHEET — INDONESIA — Reference REFERENCE WORKBOOK BASELINE (BS EN 62305-2)
Governing Standard: BS EN 62305-2:2012 / IEC 62305-2:2010 ¦ Meteorological Authority: Reference Calculation Sheet Baseline (TD=22, Graphical Ad=61,911m²) ¦ Dual-Line (Power + Telecom) & Adjacent Structure Model
Parameter / Risk Component Description | Symbol | IEC Clause / Ref | Unit / Mode | No Protection | Class IV LPS | Class III LPS | Class II LPS | Class I LPS (Target)
Structure Length | L | Annex A.2 | m | 95.6 | 95.6 | 95.6 | 95.6 | 95.6
Structure Width | W | Annex A.2 | m | 100.2 | 100.2 | 100.2 | 100.2 | 100.2
Structure Max Height | H | Annex A.2 | m | 27 | 27 | 27 | 27 | 27
Collection Area of Structure (Graphical / Complex Roof) | AD | Eq. A.3 / Graphical | m² | 61911 | 61911 | 61911 | 61911 | 61911
Location Factor of Structure | CD | Table A.1 | factor | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Thunderstorm Days per Year | TD | Meteorological | days/yr | 22 | 22 | 22 | 22 | 22
Lightning Ground Flash Density | NG | Eq. A.1 / Network | fl/km²/yr | 2.2 | 2.2 | 2.2 | 2.2 | 2.2
Annual Direct Flashes to Structure | ND | Eq. A.4 | events/yr
Collection Area of Flashes Near Structure | AM | Eq. A.7 | m²
Annual Flashes Near Structure | NM | Eq. A.6 | events/yr
Incoming Service Route Length (Power & Telecom) | LL | Table A.2 / E.2 | m | 1000 | 1000 | 1000 | 1000 | 1000
Line Installation & Environmental Product (CI × CE × CT) | CI·CE·CT | Table A.2–A.4 | factor | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Adjacent Structure Collection Area & Events (NDJ) | NDJ | Eq. A.5 | events/yr
Annual Flashes to & Near Connected Line (NL / NI per service) | NL_P / NI_P | Eq. A.8 / A.10 | events/yr
Touch & Step Voltage Protection Factor | PTA | Table B.1 | prob | 1 | 1 | 1 | 1 | 1
Physical Damage Probability (External LPS Class) | PB | Table B.2 | prob | 1 | 0.2 | 0.1 | 0.05 | 0.02
Shock Probability from Direct Flash (PA = PTA × PB) | PA | Eq. B.1 | prob
Coordinated SPD Protection Probability (PC = PSPD × CLD) | PSPD / PC | Table B.3 | prob | 1 | 0.05 | 0.05 | 0.02 | 0.01
LPS Mesh Width & Spatial Shielding Factor (wm) | wm | IEC 62305-3 | m | 0 | 60 | 45 | 30 | 20
Internal Magnetic Surge Probability (PM = PSPD × PMS) | PM | Eq. B.4 | prob
Equipotential Bonding Probability at Line Entrance (PEB) | PEB / PV | Table B.7 | prob | 0.05 | 0.05 | 0.05 | 0.02 | 0.01
Service Line Shock Probability (PU = PTU × PEB × PLD × CLD) | PU | Eq. B.8 | prob
Induced Line Surge Failure Probability (PZ_P + PZ_T) | PZ_sum | Eq. B.11 | prob
Loss Factor for Touch & Step Shock (LA1 = rt × LT1 × nZ/nt) | LA1 | Eq. C.1 | loss | 0.002 | 0.002 | 0.002 | 0.002 | 0.002
Loss Factor for Physical Fire Damage (LB1 = LV1 = rp×rf×hz×LF1×nZ/nt) | LB1 / LV1 | Eq. C.3 | loss | 0.0016 | 0.0016 | 0.0016 | 0.0016 | 0.0016
Loss Factor for Internal Systems Failure (LC1 / LC2 / LC4) | LC2 (Pub) | Eq. C.8 | loss | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RA: Injury due to Touch & Step Voltage (Direct Strike S1) | RA (×10⁻⁵) | ND×PA×LA1 | ×10⁻⁵/yr
RB: Physical Fire Damage to Structure (Direct Strike S1) | RB (×10⁻⁵) | ND×PB×LB1 | ×10⁻⁵/yr
RC + RM: Failure of Internal Systems (S1 + S2) | RC+RM (×10⁻⁵) | IEC Table 2 | ×10⁻⁵/yr
RU (Power + Telecom): Injury via Incoming Service Lines (S3) | RU (×10⁻⁵) | 2×(NL+NDJ)×PU×LU1 | ×10⁻⁵/yr
RV (Power + Telecom): Physical Fire via Service Lines (S3) | RV (×10⁻⁵) | 2×(NL+NDJ)×PV×LV1 | ×10⁻⁵/yr
RW + RZ (Power + Telecom): Internal Failure via Lines (S3 + S4) | RW+RZ (×10⁻⁵) | IEC Table 2 | ×10⁻⁵/yr
TOTAL RISK R1: Loss of Human Life (Limit RT1 = 1.00 × 10⁻⁵) | R1 (×10⁻⁵) | Sum(RA..RZ) | ×10⁻⁵/yr
TOTAL RISK R2: Loss of Public Service (Limit RT2 = 1.00 × 10⁻³) | R2 (×10⁻³) | IEC Eq. 2 | ×10⁻³/yr
TOTAL RISK R4: Economic Value Loss (Limit RT4 = 1.00 × 10⁻³) | R4 (×10⁻³) | IEC Eq. 4 | ×10⁻³/yr
Statutory Compliance Verdict (R1 ≤ 1.00e-5 AND R2 ≤ 1.00e-3) | Verdict | IEC 62305-2 Sec 5.3 | PASS / FAIL
IEC 62305-2 Ed.3 Simplified Single-Line Mode R1 (1 Line, No Adj NDJ) | R1_Ed3 (×10⁻⁵) | Ed.3 Single-Line | ×10⁻⁵/yr

## IDN_Cikarang_Tropical
IEC 62305-2 / BS EN 62305-2 LIGHTNING RISK CALCULATION SHEET — INDONESIA — GREATER JAKARTA / CIKARANG TROPICAL HYPERSCALE DC (TD=140)
Governing Standard: SNI 03-7015-2004 / IEC 62305-2:2010 (Kementerian ESDM / PLN) ¦ Meteorological Authority: BMKG Indonesia (Td=140 days/yr, Ng=13.50 fl/km²/yr) ¦ Dual-Line (Power + Telecom) & Adjacent Structure Model
Parameter / Risk Component Description | Symbol | IEC Clause / Ref | Unit / Mode | No Protection | Class IV LPS | Class III LPS | Class II LPS | Class I LPS (Target)
Structure Length | L | Annex A.2 | m | 95.6 | 95.6 | 95.6 | 95.6 | 95.6
Structure Width | W | Annex A.2 | m | 100.2 | 100.2 | 100.2 | 100.2 | 100.2
Structure Max Height | H | Annex A.2 | m | 27 | 27 | 27 | 27 | 27
Collection Area of Structure (Graphical / Complex Roof) | AD | Eq. A.3 / Graphical | m² | 61911 | 61911 | 61911 | 61911 | 61911
Location Factor of Structure | CD | Table A.1 | factor | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Thunderstorm Days per Year | TD | Meteorological | days/yr | 140 | 140 | 140 | 140 | 140
Lightning Ground Flash Density | NG | Eq. A.1 / Network | fl/km²/yr | 13.5 | 13.5 | 13.5 | 13.5 | 13.5
Annual Direct Flashes to Structure | ND | Eq. A.4 | events/yr
Collection Area of Flashes Near Structure | AM | Eq. A.7 | m²
Annual Flashes Near Structure | NM | Eq. A.6 | events/yr
Incoming Service Route Length (Power & Telecom) | LL | Table A.2 / E.2 | m | 500 | 500 | 500 | 500 | 500
Line Installation & Environmental Product (CI × CE × CT) | CI·CE·CT | Table A.2–A.4 | factor | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Adjacent Structure Collection Area & Events (NDJ) | NDJ | Eq. A.5 | events/yr
Annual Flashes to & Near Connected Line (NL / NI per service) | NL_P / NI_P | Eq. A.8 / A.10 | events/yr
Touch & Step Voltage Protection Factor | PTA | Table B.1 | prob | 1 | 0.01 | 0.01 | 0.01 | 0.01
Physical Damage Probability (External LPS Class) | PB | Table B.2 | prob | 1 | 0.2 | 0.1 | 0.05 | 0.01
Shock Probability from Direct Flash (PA = PTA × PB) | PA | Eq. B.1 | prob
Coordinated SPD Protection Probability (PC = PSPD × CLD) | PSPD / PC | Table B.3 | prob | 1 | 0.05 | 0.05 | 0.02 | 0.01
LPS Mesh Width & Spatial Shielding Factor (wm) | wm | IEC 62305-3 | m | 0 | 60 | 45 | 30 | 20
Internal Magnetic Surge Probability (PM = PSPD × PMS) | PM | Eq. B.4 | prob
Equipotential Bonding Probability at Line Entrance (PEB) | PEB / PV | Table B.7 | prob | 0.05 | 0.05 | 0.05 | 0.02 | 0.01
Service Line Shock Probability (PU = PTU × PEB × PLD × CLD) | PU | Eq. B.8 | prob
Induced Line Surge Failure Probability (PZ_P + PZ_T) | PZ_sum | Eq. B.11 | prob
Loss Factor for Touch & Step Shock (LA1 = rt × LT1 × nZ/nt) | LA1 | Eq. C.1 | loss | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05
Loss Factor for Physical Fire Damage (LB1 = LV1 = rp×rf×hz×LF1×nZ/nt) | LB1 / LV1 | Eq. C.3 | loss | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05
Loss Factor for Internal Systems Failure (LC1 / LC2 / LC4) | LC2 (Pub) | Eq. C.8 | loss | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
RA: Injury due to Touch & Step Voltage (Direct Strike S1) | RA (×10⁻⁵) | ND×PA×LA1 | ×10⁻⁵/yr
RB: Physical Fire Damage to Structure (Direct Strike S1) | RB (×10⁻⁵) | ND×PB×LB1 | ×10⁻⁵/yr
RC + RM: Failure of Internal Systems (S1 + S2) | RC+RM (×10⁻⁵) | IEC Table 2 | ×10⁻⁵/yr
RU (Power + Telecom): Injury via Incoming Service Lines (S3) | RU (×10⁻⁵) | 2×(NL+NDJ)×PU×LU1 | ×10⁻⁵/yr
RV (Power + Telecom): Physical Fire via Service Lines (S3) | RV (×10⁻⁵) | 2×(NL+NDJ)×PV×LV1 | ×10⁻⁵/yr
RW + RZ (Power + Telecom): Internal Failure via Lines (S3 + S4) | RW+RZ (×10⁻⁵) | IEC Table 2 | ×10⁻⁵/yr
TOTAL RISK R1: Loss of Human Life (Limit RT1 = 1.00 × 10⁻⁵) | R1 (×10⁻⁵) | Sum(RA..RZ) | ×10⁻⁵/yr
TOTAL RISK R2: Loss of Public Service (Limit RT2 = 1.00 × 10⁻³) | R2 (×10⁻³) | IEC Eq. 2 | ×10⁻³/yr
TOTAL RISK R4: Economic Value Loss (Limit RT4 = 1.00 × 10⁻³) | R4 (×10⁻³) | IEC Eq. 4 | ×10⁻³/yr
Statutory Compliance Verdict (R1 ≤ 1.00e-5 AND R2 ≤ 1.00e-3) | Verdict | IEC 62305-2 Sec 5.3 | PASS / FAIL
IEC 62305-2 Ed.3 Simplified Single-Line Mode R1 (1 Line, No Adj NDJ) | R1_Ed3 (×10⁻⁵) | Ed.3 Single-Line | ×10⁻⁵/yr

## MYS_Johor_DataCenter
IEC 62305-2 / BS EN 62305-2 LIGHTNING RISK CALCULATION SHEET — MALAYSIA — JOHOR BAHRU (ISKANDAR) & KL HYPERSCALE DATA CENTER (TD=165)
Governing Standard: MS IEC 62305 / Suruhanjaya Tenaga (Energy Commission Malaysia) ¦ Meteorological Authority: MetMalaysia (Td=165 days/yr, Ng=14.20 fl/km²/yr) ¦ Dual-Line (Power + Telecom) & Adjacent Structure Model
Parameter / Risk Component Description | Symbol | IEC Clause / Ref | Unit / Mode | No Protection | Class IV LPS | Class III LPS | Class II LPS | Class I LPS (Target)
Structure Length | L | Annex A.2 | m | 90 | 90 | 90 | 90 | 90
Structure Width | W | Annex A.2 | m | 65 | 65 | 65 | 65 | 65
Structure Max Height | H | Annex A.2 | m | 26 | 26 | 26 | 26 | 26
Collection Area of Isolated Structure | AD | Eq. A.2 | m²
Location Factor of Structure | CD | Table A.1 | factor | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Thunderstorm Days per Year | TD | Meteorological | days/yr | 165 | 165 | 165 | 165 | 165
Lightning Ground Flash Density | NG | Eq. A.1 / Network | fl/km²/yr | 14.2 | 14.2 | 14.2 | 14.2 | 14.2
Annual Direct Flashes to Structure | ND | Eq. A.4 | events/yr
Collection Area of Flashes Near Structure | AM | Eq. A.7 | m²
Annual Flashes Near Structure | NM | Eq. A.6 | events/yr
Incoming Service Route Length (Power & Telecom) | LL | Table A.2 / E.2 | m | 400 | 400 | 400 | 400 | 400
Line Installation & Environmental Product (CI × CE × CT) | CI·CE·CT | Table A.2–A.4 | factor | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Adjacent Structure Collection Area & Events (NDJ) | NDJ | Eq. A.5 | events/yr
Annual Flashes to & Near Connected Line (NL / NI per service) | NL_P / NI_P | Eq. A.8 / A.10 | events/yr
Touch & Step Voltage Protection Factor | PTA | Table B.1 | prob | 1 | 0.01 | 0.01 | 0.01 | 0.01
Physical Damage Probability (External LPS Class) | PB | Table B.2 | prob | 1 | 0.2 | 0.1 | 0.05 | 0.01
Shock Probability from Direct Flash (PA = PTA × PB) | PA | Eq. B.1 | prob
Coordinated SPD Protection Probability (PC = PSPD × CLD) | PSPD / PC | Table B.3 | prob | 1 | 0.05 | 0.05 | 0.02 | 0.01
LPS Mesh Width & Spatial Shielding Factor (wm) | wm | IEC 62305-3 | m | 0 | 60 | 45 | 30 | 20
Internal Magnetic Surge Probability (PM = PSPD × PMS) | PM | Eq. B.4 | prob
Equipotential Bonding Probability at Line Entrance (PEB) | PEB / PV | Table B.7 | prob | 0.05 | 0.05 | 0.05 | 0.02 | 0.01
Service Line Shock Probability (PU = PTU × PEB × PLD × CLD) | PU | Eq. B.8 | prob
Induced Line Surge Failure Probability (PZ_P + PZ_T) | PZ_sum | Eq. B.11 | prob
Loss Factor for Touch & Step Shock (LA1 = rt × LT1 × nZ/nt) | LA1 | Eq. C.1 | loss | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05
Loss Factor for Physical Fire Damage (LB1 = LV1 = rp×rf×hz×LF1×nZ/nt) | LB1 / LV1 | Eq. C.3 | loss | 8e-05 | 8e-05 | 8e-05 | 8e-05 | 8e-05
Loss Factor for Internal Systems Failure (LC1 / LC2 / LC4) | LC2 (Pub) | Eq. C.8 | loss | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
RA: Injury due to Touch & Step Voltage (Direct Strike S1) | RA (×10⁻⁵) | ND×PA×LA1 | ×10⁻⁵/yr
RB: Physical Fire Damage to Structure (Direct Strike S1) | RB (×10⁻⁵) | ND×PB×LB1 | ×10⁻⁵/yr
RC + RM: Failure of Internal Systems (S1 + S2) | RC+RM (×10⁻⁵) | IEC Table 2 | ×10⁻⁵/yr
RU (Power + Telecom): Injury via Incoming Service Lines (S3) | RU (×10⁻⁵) | 2×(NL+NDJ)×PU×LU1 | ×10⁻⁵/yr
RV (Power + Telecom): Physical Fire via Service Lines (S3) | RV (×10⁻⁵) | 2×(NL+NDJ)×PV×LV1 | ×10⁻⁵/yr
RW + RZ (Power + Telecom): Internal Failure via Lines (S3 + S4) | RW+RZ (×10⁻⁵) | IEC Table 2 | ×10⁻⁵/yr
TOTAL RISK R1: Loss of Human Life (Limit RT1 = 1.00 × 10⁻⁵) | R1 (×10⁻⁵) | Sum(RA..RZ) | ×10⁻⁵/yr
TOTAL RISK R2: Loss of Public Service (Limit RT2 = 1.00 × 10⁻³) | R2 (×10⁻³) | IEC Eq. 2 | ×10⁻³/yr
TOTAL RISK R4: Economic Value Loss (Limit RT4 = 1.00 × 10⁻³) | R4 (×10⁻³) | IEC Eq. 4 | ×10⁻³/yr
Statutory Compliance Verdict (R1 ≤ 1.00e-5 AND R2 ≤ 1.00e-3) | Verdict | IEC 62305-2 Sec 5.3 | PASS / FAIL
IEC 62305-2 Ed.3 Simplified Single-Line Mode R1 (1 Line, No Adj NDJ) | R1_Ed3 (×10⁻⁵) | Ed.3 Single-Line | ×10⁻⁵/yr

## IEC62305_3_4_LPS_SPD
IEC 62305-3 & 62305-4 PHYSICAL LPS DESIGN, ROLLING SPHERE (r), SEPARATION DISTANCE (s) & SPD SCHEDULE
Covers Air-Termination Mesh (wm), Rolling Sphere Radius (r), Rooftop Cooling Tower Rod Protection (rp), Side-Flash Separation (s), and LPZ 0A/1/2/3 SPDs
Regional Facility Profile | Selected LPS Class | Rolling Sphere r (m) | Air Mesh wm (m×m) | Down-Cond. Spacing dw (m) | Total Down-Conductors Ndc | Rooftop Mast Protected Radius rp (m) | Min Separation Distance s (m) | Earthing Grid Resistance RE (Ω)
Hong Kong TKO Hyperscale DC | Class I (LPL I) | 20 | 5 × 5 m | 10
Indonesia Reference Reference Baseline | Class I (LPL I) | 20 | 5 × 5 m | 10
Indonesia Cikarang Tropical DC (TD=140) | Class I Enhanced (Metal Roof + Natural Down-Cond) | 20 | 5 × 5 m | 10
Malaysia Johor Bahru / KL DC (TD=165) | Class I Enhanced (Metal Roof + Natural Down-Cond) | 20 | 5 × 5 m | 10
IEC 62305-4 Coordinated Surge Protective Device (SPD) & Adiabatic Earthing Schedule
LPZ Boundary | Installation Location (Switchboard / Panel) | SPD Type / Class (IEC 61643-11) | Test Waveform | Min Discharge Rating (LPL I) | Voltage Protection Level Up | Coordinated PSPD Factor | Min Copper Bonding Cross-Section | Statutory Clause Reference
LPZ 0A -> LPZ 1 | LV Main Switchboard (MSB / ACB Incomer) | Type 1 + Type 2 Combined SPD | 10/350 µs + 8/20 µs | Iimp ≥ 25 kA/pole (100 kA total) | Up ≤ 1.5 kV | 0.01 | 50 mm² Cu (Main Earth Bar) | IEC 62305-4 Cl. 7 / Table B.3
LPZ 1 -> LPZ 2 | UPS Input/Output & Data Hall PDU / SDB | Type 2 Coordinated SPD | 8/20 µs | In ≥ 20 kA, Imax ≥ 40 kA/pole | Up ≤ 1.2 kV | 0.01 | 16 mm² Cu | IEC 62305-4 Cl. 7.3
LPZ 2 -> LPZ 3 | Server Rack RPP / Critical BMS & PLC Panel | Type 2 + Type 3 Fine Hybrid SPD | 8/20 µs + 1.2/50 µs | In ≥ 10 kA, Uoc = 6 kV | Up ≤ 0.8 kV | 0.005 | 6 mm² Cu | IEC 62305-4 Annex C
LPZ 0A -> LPZ 1 (Telecom) | MDF / Fiber Metallic Armor & Copper Telecom Entry | Category D1 High-Energy Telecom SPD | 10/350 µs | Iimp ≥ 2.5 kA/line | Up ≤ 0.6 kV | 0.01 | 16 mm² Cu to MET | IEC 61643-21 / IEC 62305-4
IEC 62305-3 Multi-Level Rolling Sphere (r = 20/30/45/60m) Rooftop Cooling Tower Blind-Spot & Separation Distance s = (ki/km)·kc·l Verification Matrix (hrod=6.0m, heq=3.5m, Weq=4.5m, dhoriz=1.5m)
LPS Class / Lightning Protection Level | Rolling Sphere Radius r (m) | Ground Touchdown Reach xc (m) | Protected Radius rp at heq=3.5m (m) | Sphere Arc Height at Equipment Far Edge x=6.0m (m) | Blind-Spot Protrusion Depth Δh_blind (m) | Induction Factor ki (IEC Table 10) | Required Separation s = (ki/km)·kc·l (m) | Blind-Spot & Side-Flash Verdict (d_actual = 1.50m)
Class I LPS (LPL I — PB = 0.02) | 20 |  |  |  |  | 0.08
Class II LPS (LPL II — PB = 0.05) | 30 |  |  |  |  | 0.06
Class III LPS (LPL III — PB = 0.10) | 45 |  |  |  |  | 0.04
Class IV LPS (LPL IV — PB = 0.20) | 60 |  |  |  |  | 0.04

## Campus_MultiBuilding_Batch
MULTI-BUILDING CAMPUS BATCH LIGHTNING RISK & LPS SCHEDULE (SCANNED FROM PDF / DWG / DXF / BIM SITE PLAN)
Standard: IEC 62305-2:2010 Annex A (Eq. A.2 & Table A.1) ¦ Option A Locked: Full Outer Envelope (142.7m × 101.9m × 30.0m, heq=5.1m) + 6-Building Master Campus (v2.5.0)
Building ID & Designation | Facility Classification | Length L (m) | Width W (m) | Height H (m) | Collection Area AD (m²) | Spatial Factor Cd (Table A.1) | Direct Strikes ND (/yr) | Unprotected R1 (×10⁻⁵) | Selected LPS Class | Protected R1 (×10⁻⁵) | Rolling Sphere r / Min Sep s
DCH-01 | Hyperscale Data Hall Alpha (Building A) | 95.6 | 100.2 | 27 |  | 0.5 |  |  | Class I Enhanced (PB=0.01)
DCH-02 | Hyperscale Data Hall Beta (Building B) | 95.6 | 100.2 | 27 |  | 0.5 |  |  | Class I Enhanced (PB=0.01)
SUB-03 | 150kV/20kV GIS Main Substation | 42 | 26 | 11.5 |  | 0.25 |  |  | Class I LPS (PB=0.02)
CUP-04 | Central Utility & Standby Generator Plant | 68 | 34 | 16 |  | 0.25 |  |  | Class I LPS (PB=0.02)
ADM-05 | Administration, NOC & Security Block | 50 | 28 | 19.5 |  | 0.5 |  |  | Class II LPS (PB=0.05)
FUEL-06 | Bulk B40 Diesel Storage Tank Farm | 32 | 18 | 8 |  | 0.25 |  |  | Class I Enhanced (PB=0.01)
CAMPUS TOTAL / MAX | 6 Scanned Campus Structures (All Protected R1 ≤ 1.00e-5) | [7 empty] | 100% Campus Compliant |  | PASS (6/6 Buildings)